{"text_format":"3","workbook":"xlsx","n_sheets":2,"sheets":["污水提升泵站","雨水提升泵站"],"read":"whole","date_system":"1900"}

{"sheet":"污水提升泵站","index":0,"n_rows":30,"n_cols":8,"rows_kept":30,"merged":[[0,0,0,7],[28,0,28,6],[29,0,29,6]]}
["污水一体化泵站"]
["序号","名称","材质","规格","单位","数量","说明","品牌推荐表有要求的请注明所投产品品牌"]
[1,"泵站筒体","无碱缠绕玻璃钢GRP/模量聚丙烯HMPP","直径1200mm，高度4500mm","台",1,"具有CMA和CNAS双重认证机\n构的质检报告"]
[2,"污水泵",null,"Q=2m3/h,H=10m\n N=0.75kw\n一用一备","台",2,"威乐、凯士比、格兰富"]
[3,"水泵导轨","SUS304",null,"套",2,"含SUS304提升链"]
[4,"自耦底座","HT200","DN50","套",2]
[5,"液位仪保护管","UPVC","DN50","套",1,"放置静压液位仪，根据液位\n控制水泵启停  "]
[6,"压力管道","SUS304","DN65","套",2,"壁厚不低于3mm"]
[7,"止回阀","HT250","DN65","套",2]
[8,"闸阀","HT250","DN65","套",2]
[9,"吊耳","Q235",null,"套",1]
[10,"出水口软连接","可曲挠橡胶","JGD41-10DN80","套",1]
[11,"进水口软连接","可曲挠橡胶","JGD41-10DN300","套",1]
[12,"粉碎格栅","SUS304",null,"套",1]
[13,"格栅导轨","SUS304","根据筒体配套定制尺寸，含提升链","套",1]
[14,"格栅支架","SUS304","根据筒体配套定制尺寸","套",1]
[15,"服务平台","GRP格栅板 SUS304","不低于1.13㎡","套",1,"日常在平台上检修和维护设 备使用"]
[16,"扶梯","SUS304","根据筒体配套定制尺寸","套",1,"50*30mm"]
[17,"盖板","压花铝板","根据筒体配套定制尺寸","套",1,"不低于4mm厚"]
[18,"安全格栅","GRP格栅板 SUS304","根据筒体配套定制尺寸","套",1]
[19,"扶手","SUS304",null,"套",1]
[20,"通风管","SUS304","DN80","套",1]
[21,"智能控制柜","不锈钢防水户外型","一控二，0.75kw","套",1,"304不锈钢户外型，防雨型，触摸屏，防雷击浪涌装置，预留485通讯接口，元器件：ABB、西门子、施耐德。"]
[22,"液位浮球",null,null,"套",1,"传感器坏时备用，自动控制\n水泵启停"]
[23,"一体化格栅闸门 井","GRP/HMPP","直径1200mm，高度\n4500mm","套",1,"含：手动启闭机，不锈钢闸\n门DN300，可提拉格栅（栅\n空40*40）"]
[24,"智能UV离子除臭仪","不锈钢防水户外型组合件","风量2000m3/h，N=2.2KW，静音风机","套",1]
[25,"汇总管","SUS304","DN80","套",1,"两组泵出水管汇总成一根DN80管排出"]
[26,"异径同芯大小头","SUS304","DN50-65","套",2]
["人民币大写：               （¥            ）。"]
["说明：水泵参考品牌为威乐(Wilo)、凯士比、格兰富，其余参照甲方要求的主要材料品牌推荐表。"]

{"sheet":"雨水提升泵站","index":1,"n_rows":28,"n_cols":8,"rows_kept":28,"merged":[[0,0,0,7],[26,0,26,6],[27,0,27,6]]}
["雨水一体化泵站"]
["序号","名称","材质","规格","单位","数量","备注说明","品牌推荐表有要求的请注明所投产品品牌"]
[1,"泵站筒体","无碱缠绕玻璃钢GRP","直径4200mm，高度\n6300mm","台",1,"具有CMA和CNAS双重认证机\n构的质检报告"]
[2,"污水泵",null,"Q=1500m3/h,H=12m N=90kw 两用一备","台",3]
[3,"水泵导轨","SUS304",null,"套",3,"含SUS304提升链"]
[4,"自耦底座","HT200","DN300","套",3]
[5,"液位仪保护管","UPVC","DN50","套",1,"放置静压液位仪，根据液位\n控制水泵启停  "]
[6,"压力管道","SUS304","DN350","套",3]
[7,"止回阀","HT250","DN350","套",3]
[8,"闸阀","HT250","DN350","套",3]
[9,"出水口软连接","可曲挠橡胶","JGD41-10DN600","套",1]
[10,"进水口软连接","可曲挠橡胶","JGD41-10DN1200","套",1]
[11,"提篮格栅","SUS304",null,"套",1]
[12,"格栅导轨","SUS304","含提升链","套",1]
[13,"格栅支架","SUS304",null,"套",1]
[14,"服务平台","GRP格栅板 SUS304","不低于14平方","套",1,"日常在平台上检修和维护设 备使用"]
[15,"扶梯","SUS304","根据筒体配套定制尺寸","套",1]
[16,"盖板","压花铝板","根据筒体配套定制尺寸","套",1]
[17,"安全格栅","GRP格栅板 SUS304","根据筒体配套定制尺寸","套",1]
[18,"扶手","SUS304",null,"套",1]
[19,"通风管",null,null,"套",1]
[20,"智能控制柜","不锈钢防水户外\n型","一控三，90kw","套",1,"304不锈钢户外型，防雨型，触摸屏，防雷击浪涌装置，预留485通讯接口，元器件：ABB、西门子、施耐德。"]
[21,"液位浮球",null,null,"套",1,"传感器坏时备用，自动控制\n水泵启停"]
[22,"90度弯头","SUS304","DN350","套",3]
[23,"异径同心大小头","SUS304","DN350-300","套",3]
[24,"吊耳","Q235",null,"套",1]
["人民币大写：               （¥            ）。"]
["说明：水泵参考品牌为凯泉、奥利、熊猫，其余参照甲方要求的主要材料品牌推荐表。"]